## Step 1 - Calc System Watts Amps
Directions: | In the gray space provided to the right of the zone number, enter that zones amperage.
NOTE: Heater Voltage is:-------------------------------- |  |  |  | 240 | VAC
Zone 1 to 30 | Amps |  | Zone 31 to 60 | Amps |  | Zone 61 to 90 | Amps | Zone 91 to 120 | Amps |  | Zone 121 to 150 | Amps | Zone 151 to 180 | Amps
Zone 1 | 3.96 |  | Zone 31 | 3.96 |  | Zone 61 | 3.96 | Zone 91 | 0 |  | Zone 121 | 0 | Zone 151 | 0
Zone 2 | 3.96 |  | Zone 32 | 3.96 |  | Zone 62 | 3.96 | Zone 92 | 0 |  | Zone 122 | 0 | Zone 152 | 0
Zone 3 | 3.96 |  | Zone 33 | 3.96 |  | Zone 63 | 3.96 | Zone 93 | 0 |  | Zone 123 | 0 | Zone 153 | 0
Zone 4 | 3.96 |  | Zone 34 | 3.96 |  | Zone 64 | 3.96 | Zone 94 | 0 |  | Zone 124 | 0 | Zone 154 | 0
Zone 5 | 3.96 |  | Zone 35 | 3.96 |  | Zone 65 | 3.96 | Zone 95 | 0 |  | Zone 125 | 0 | Zone 155 | 0
Zone 6 | 3.96 |  | Zone 36 | 3.96 |  | Zone 66 | 3.96 | Zone 96 | 0 |  | Zone 126 | 0 | Zone 156 | 0
Zone 7 | 3.96 |  | Zone 37 | 3.96 |  | Zone 67 | 3.96 | Zone 97 | 0 |  | Zone 127 | 0 | Zone 157 | 0
Zone 8 | 3.96 |  | Zone 38 | 3.96 |  | Zone 68 | 3.96 | Zone 98 | 0 |  | Zone 128 | 0 | Zone 158 | 0
Zone 9 | 3.96 |  | Zone 39 | 3.96 |  | Zone 69 | 3.96 | Zone 99 | 0 |  | Zone 129 | 0 | Zone 159 | 0
Zone 10 | 3.96 |  | Zone 40 | 3.96 |  | Zone 70 | 3.96 | Zone 100 | 0 |  | Zone 130 | 0 | Zone 160 | 0
Zone 11 | 3.96 |  | Zone 41 | 3.96 |  | Zone 71 | 3.96 | Zone 101 | 0 |  | Zone 131 | 0 | Zone 161 | 0
Zone 12 | 3.96 |  | Zone 42 | 3.96 |  | Zone 72 | 3.96 | Zone 102 | 0 |  | Zone 132 | 0 | Zone 162 | 0
Zone 13 | 3.96 |  | Zone 43 | 3.96 |  | Zone 73 | 0 | Zone 103 | 0 |  | Zone 133 | 0 | Zone 163 | 0
Zone 14 | 3.96 |  | Zone 44 | 3.96 |  | Zone 74 | 0 | Zone 104 | 0 |  | Zone 134 | 0 | Zone 164 | 0
Zone 15 | 3.96 |  | Zone 45 | 3.96 |  | Zone 75 | 0 | Zone 105 | 0 |  | Zone 135 | 0 | Zone 165 | 0
Zone 16 | 3.96 |  | Zone 46 | 3.96 |  | Zone 76 | 0 | Zone 106 | 0 |  | Zone 136 | 0 | Zone 166 | 0
Zone 17 | 3.96 |  | Zone 47 | 3.96 |  | Zone 77 | 0 | Zone 107 | 0 |  | Zone 137 | 0 | Zone 167 | 0
Zone 18 | 3.96 |  | Zone 48 | 3.96 |  | Zone 78 | 0 | Zone 108 | 0 |  | Zone 138 | 0 | Zone 168 | 0
Zone 19 | 3.96 |  | Zone 49 | 3.96 |  | Zone 79 | 0 | Zone 109 | 0 |  | Zone 139 | 0 | Zone 169 | 0
Zone 20 | 3.96 |  | Zone 50 | 3.96 |  | Zone 80 | 0 | Zone 110 | 0 |  | Zone 140 | 0 | Zone 170 | 0
Zone 21 | 3.96 |  | Zone 51 | 3.96 |  | Zone 81 | 0 | Zone 111 | 0 |  | Zone 141 | 0 | Zone 171 | 0
Zone 22 | 3.96 |  | Zone 52 | 3.96 |  | Zone 82 | 0 | Zone 112 | 0 |  | Zone 142 | 0 | Zone 172 | 0
Zone 23 | 3.96 |  | Zone 53 | 3.96 |  | Zone 83 | 0 | Zone 113 | 0 |  | Zone 143 | 0 | Zone 173 | 0
Zone 24 | 3.96 |  | Zone 54 | 3.96 |  | Zone 84 | 0 | Zone 114 | 0 |  | Zone 144 | 0 | Zone 174 | 0
Zone 25 | 3.96 |  | Zone 55 | 3.96 |  | Zone 85 | 0 | Zone 115 | 0 |  | Zone 145 | 0 | Zone 175 | 0
Zone 26 | 3.96 |  | Zone 56 | 3.96 |  | Zone 86 | 0 | Zone 116 | 0 |  | Zone 146 | 0 | Zone 176 | 0
Zone 27 | 3.96 |  | Zone 57 | 3.96 |  | Zone 87 | 0 | Zone 117 | 0 |  | Zone 147 | 0 | Zone 177 | 0
Zone 28 | 3.96 |  | Zone 58 | 3.96 |  | Zone 88 | 0 | Zone 118 | 0 |  | Zone 148 | 0 | Zone 178 | 0
Zone 29 | 3.96 |  | Zone 59 | 3.96 |  | Zone 89 | 0 | Zone 119 | 0 |  | Zone 149 | 0 | Zone 179 | 0
Zone 30 | 3.96 |  | Zone 60 | 3.96 |  | Zone 90 | 0 | Zone 120 | 0 |  | Zone 150 | 0 | Zone 180 | 0
Total System AMPS (Single Phase) is: | [8 empty] | 285.12 | Total System Amps
Amperage Required for the INPUT or Primary side of the transformer is: | [8 empty] | 59.4 | Amps Three Phase Required Min
| 39.5074 | KVA
| 480 | Primary Volts AC
The calculated system KVA requirement is: | [8 empty] | 39.5074 | KVA Three Phase
| 285.12 | Total Amps
| 95.04 | Single Phase Amps
| 240 | Secondary Volts AC
The Transformer KVA required is: | [8 empty] | 45
If this is a Pulse, Transformer Kit Part Number is | [8 empty] | See Design Engineer for Help
(Rack is included)
If this is a Pulse 2, Transformer Kit Part Number is | [8 empty] | KD021008
(Rack is NOT included)

## Step 2 - Calculate Requirements
The Amperage Required for the INPUT or Primary side of the transformer is: | [5 empty] | 59.4 | Amps Three Phase Required Minimum
| 39.5074 | KVA
| 480 | Primary Volts AC
Note: This is the calculated minimum current at full load for the given system in Step 1.
The calculated system KVA requirement is: |  |  |  | ____________________________________________ |  | 39.5074 | KVA Three Phase
| 285.12 | Total Amps
| 95.04 | Single Phase Amps
| 240 | Secondary Volts AC
Note: This is the calculated KVA required at full load current for the given system in Step 1.
The Transformer KVA required is: |  |  | _____________________________________________________ |  |  | 45
If this is a Pulse, Transformer Kit Part Number is |  |  |  |  | ___________________________________ | See Design Engineer for Help
(Rack is included)
If this is a Pulse 2, Transformer Kit Part Number is |  |  |  |  | ___________________________________ | KD021008
(Rack is NOT included)